## SOCO
SOCO
Geograhic Boundary: |  |  | SE Mississippi, Alabama, Georgia, & Florida panhandle
Fuel Sources:
COAL
|  | Appalachia | Ill Basin | S. PRB | Other | Imports
| % Delivered | 52% | 14% | 29% | 4% | 1%
| MS T&H | 13.98 | 10.7 | 19
| AL/FL T&H | 11.01 | 7.12 | 21
| GA T&H | 12.11 | 11.04 | 21
| BTU Content | 12000 | 11300 | 8600
| Conversion | 0.041667 | 0.044248 | 0.05814
| Natural Gas |  | Southern Co., the main ute pulls off of SONAT which historically trades -.02 to Henry hub
| FO2/FO6 |  | Use Gulf Coast Resid and Heating Oil prices, with minimal variable costs
FO6(resid) is qouted in $/Bl, conversion is .1586
FO2(HO) is quoted in Cents/Gallon, conversion is 7.17
| Rivers with Dams: |  | Chattahochie River & Tennessee River comprise 95% of Hydro sources
Load Mix: |  | Type | %
|  | Residential | 37%
|  | Commercial | 26.4%
|  | Industrial | 35.6%
|  | Pub/St Hwy Lt | 0.4%
|  | Other | 0.6%
100%
Stack/Outages:
[5 empty] | Winter |  |  |  | Summer |  |  |  | Marginal | Summer | Winter
|  |  | Winter | New | Total | % | Summer | New | Total | % | Fuel | $ | MW(h) | Increm | Increm
| Fuel Type | HeatRate | Cap | Cap | Cap | Cap | Cap | Cap | Cap | Cap | Cost | mmbtu | Cost | MW | MW
| Hydro | 0.01 | 5249 | 0 | 5249 | 10.04% | 5276 | 0 | 5276 | 10.25% | 0.25 | 0.25 | 0.0025 | 5276 | 5249
| Nuke | 10930 | 5774 | 0 | 5774 | 11.04% | 5774 | 0 | 5774 | 11.21% | 0.5 | 0.5 | 5.465 | 11050 | 11023
| Coal | 9791 | 26017 | 0 | 26017 | 49.76% | 25984 | 0 | 25984 | 50.46% | 38 | 1.5833 | 15.5024 | 37034 | 37040
| NG-CC | 8138 | 5225 | 0 | 5225 | 9.993% | 5161 | 0 | 5161 | 10.02% | 2 | 2 | 16.276 | 42195 | 42265
| NG-CT | 12142 | 8199 | 0 | 8199 | 15.68% | 7782 | 0 | 7782 | 15.11% | 2 | 2 | 24.284 | 49977 | 50464
| FO6-Resid | 10746 | 122 | 0 | 122 | 0.2333% | 122 | 0 | 122 | 0.2369% | 14.63 | 2.32 | 24.9309 | 50099 | 50586
| FO2-HO | 13828 | 1703 | 0 | 1703 | 3.257% | 1391 | 0 | 1391 | 2.701% | 0.5205 | 3.732 | 51.6059 | 51490 | 52289
|  |  | 52289 | 0 | 52289 | 100% | 51490 | 0 | 51490 | 100%
*** SOCO has 1500MW of COGEN which could switch to the GRID if prices permit
| Capacity Additions | [5 empty] | Seasonal Demand/Outages
| Year | Gas-CC | Gas-CT | Cogen | Totals |  | 16 hr Pk | Peak Range |  | *Seasonal Interchange |  |  |  |  | **Normal
| Q1-2002 | 570 | 0 | 0 | 570 | Month | Avg. | Max | Min | ENT | VACAR | TVA | FLA | Total | Outages
| Q2-2002 | 3718 | 3562 | 0 | 7280 | Jan | 30340 | 34184 | 15912 | 539 | 552 | 440 | -2373 | -842 | 5198.45
| Q3-2002 | 0 | 0 | 240 | 240 | Feb | 26185 | 29614 | 19179 | 539 | 552 | 440 | -2373 | -842 | 8245.45
| Q4-2002 | 0 | 0 | 0 | 0 | Mar | 25560 | 29106 | 19589 | 539 | 552 | 440 | -2373 | -842 | 9998.45
| 2002 | 4288 | 3562 | 240 | 8090 | Apr | 28025 | 30306 | 18742 | 539 | 552 | 440 | -2373 | -842 | 10551.45
| Q1-2003 | 2407 | 0 | 0 | 2407 | May | 31932 | 35125 | 19584 | 411 | 414 | 650 | -2223 | -748 | 6031.45
| Q2-2003 | 2590 | 2208 | 1500 | 6298 | Jun | 34392 | 38036 | 20728 | 411 | 414 | 650 | -2223 | -748 | 2952.45
| Q3-2003 | 0 | 0 | 0 | 0 | Jul | 36597 | 41050 | 26423 | 411 | 414 | 650 | -2223 | -748 | 2811.45
| Q4-2003 | 0 | 0 | 0 | 0 | Aug | 36582 | 41489 | 24832 | 411 | 414 | 650 | -2223 | -748 | 2762.45
| 2003 | 4997 | 2208 | 1500 | 8705 | Sep | 33599 | 37382 | 21574 | 411 | 414 | 650 | -2223 | -748 | 4171.45
| Q1-2004 | 529 | 0 | 1230 | 1759 | Oct | 37934 | 31984 | 20248 | 539 | 552 | 440 | -2373 | -842 | 7794.45
| Q2-2004 | 1303 | 750 | 0 | 2053 | Nov | 27073 | 29400 | 18841 | 539 | 552 | 440 | -2373 | -842 | 8662.45
| Q3-2004 | 0 | 0 | 0 | 0 | Dec | 30683 | 34608 | 18352 | 539 | 552 | 440 | -2373 | -842 | 5766.45
| Q4-2004 | 0 | 0 | 0 | 0 |  | *A Postive interchange is "import", a Negative is "export"
| 2004 | 1832 | 750 | 1230 | 3812 |  | **Outages include 5% forced out
| TOTAL | 11117 | 6520 | 2970 | 20607
Top 5 Utes:
|  | Hydro | Nuke | Coal | NG-CC | NG-CT | FO6 | FO2 | Totals
| Georgia Pwr | 900 | 0 | 12845 | 187 | 1445 | 122 | 1106 | 16605
| Ala Pwr Co. | 1682 | 940 | 8274 | 1314 | 940 | 0 | 16 | 13166
| Southern Nuclear | 0 | 5773 | 0 | 0 | 0 | 0 | 0 | 5773
| Miss Pwr Co. | 0 | 0 | 1730 | 1437 | 0 | 0 | 0 | 3167
| Gulf Pwr Co. | 0 | 0 | 1468 | 88 | 13 | 0 | 32 | 1601
Top 5 Merchant(EOY '02):
|  | NG-CC | NG-CT | Totals
| Duke | 1240 | 640 | 1880
| Tenaska | 846 | 468 | 1314
| Morgan Stanley | 0 | 1120 | 1120
| El Paso | 0 | 680 | 680
| Dynegy | 0 | 500 | 500
Note on L39: mcarson2: $/ton 12,000 btu content big sandy NYMEX Coal + T&H Conversion factor: $ coal*.04167= $mmbtu
Note on L40: mcarson2: $/mmbtu
Note on L41: mcarson2: $/mmbtu
Note on L42: mcarson2: Gulf Coast Resid Quoted in $/Bl. Conversion is $FO6*.1586=$/mmbtu
Note on L43: mcarson2: quoted in Cents/Gal, 42 Gal per Bl. Coversion is $FO2*7.17 = $/mmbtu